## Slide 1: CHAPTER 11 REFRIGERATION CYCLES
Lecture slides by
Mehmet Kanoglu
Copyright © The McGraw-Hill Education. Permission required for reproduction or display.
Thermodynamics: An Engineering Approach
8th Edition Yunus A. Çengel, Michael A. Boles
McGraw-Hill, 2015

## Slide 2
Objectives
Introduce the concepts of refrigerators and heat pumps and the measure of their performance.
Analyze the ideal vapor-compression refrigeration cycle.
Analyze the actual vapor-compression refrigeration cycle.
Review the factors involved in selecting the right refrigerant for an application.
Discuss the operation of refrigeration and heat pump systems.
Evaluate the performance of innovative vapor-compression refrigeration systems.
Analyze gas refrigeration systems.
Introduce the concepts of absorption-refrigeration systems.

## Slide 3
REFRIGERATORS AND HEAT PUMPS
The transfer of heat from a low-temperature region to a high-temperature one requires special devices called refrigerators.
Another device that transfers heat from a low-temperature medium to a high-temperature one is the heat pump.
Refrigerators and heat pumps are essentially the same devices; they differ in their objectives only.
for fixed values of QL and QH

## Slide 4
THE REVERSED CARNOT CYCLE
Both COPs increase as the difference between the two temperatures decreases, that is, as TL rises or TH falls.
The reversed Carnot cycle is the most efficient refrig. cycle operating between TL and TH.
It is not a suitable model for refrigeration cycles since processes 2-3 and 4-1 are not practical because Process 2-3 involves the compression of a liquid–vapor mixture, which requires a compressor that will handle two phases, and process 4-1 involves the expansion of high-moisture-content refrigerant in a turbine.

## Slide 5
THE IDEAL VAPOR-COMPRESSION REFRIGERATION CYCLE
The vapor-compression refrigeration cycle is the ideal model for refrigeration systems. Unlike the reversed Carnot cycle, the refrigerant is vaporized completely before it is compressed and the turbine is replaced with a throttling device.
Schematic and T-s diagram for the ideal vapor-compression refrigeration cycle.
This is the most widely used cycle for refrigerators, A-C systems, and heat pumps.

## Slide 6
The ideal vapor-compression refrigeration cycle involves an irreversible (throttling) process to make it a more realistic model for the actual systems.
Replacing the expansion valve by a turbine is not practical since the added benefits cannot justify the added cost and complexity.
Steady-flow energy balance

## Slide 7
ACTUAL VAPOR-COMPRESSION REFRIGERATION CYCLE
An actual vapor-compression refrigeration cycle differs from the ideal one owing mostly to the irreversibilities that occur in various components, mainly due to fluid friction (causes pressure drops) and heat transfer to or from the surroundings.
DIFFERENCES
Non-isentropic compression
Superheated vapor at evaporator exit
Subcooled liquid at condenser exit
Pressure drops in condenser and evaporator
The COP decreases as a result of irreversibilities.

## Slide 8
SECOND-LAW ANALYSIS OF VAPOR-COMPRESSION REFRIGERATION CYCLE
The maximum COP of a refrigeration cycle operating between temperature limits of TL and TH
Actual refrigeration cycles are not as efficient as ideal ones like the Carnot cycle because of the irreversibilities involved. But the conclusion we can draw from Eq. 11–9 that the COP is inversely proportional to the temperature difference TH - TL is equally valid for actual refrigeration cycles.
The goal of a second-law or exergy analysis of a refrigeration system is to determine the components that can benefit the most by improvements.
This is done identifying the locations of greatest exergy destruction and the components with the lowest exergy or second-law efficiency.
Exergy destruction in a component can be determined directly from an exergy balance or by using

## Slide 9
Note that when TH = T0, which is often the case for refrigerators, II,cond = 0 since there is no recoverable exergy in this case.

## Slide 10
The exergy rate associated with the withdrawal of heat from the low-temperature medium at TL at a rate of QL
This is equivalent to the power that can be produced by a Carnot heat engine receiving heat from the environment at T0 and rejecting heat to the low temperature medium at TL at a rate of QL.
Note that when TL = T0, which is often the case for heat pumps, II,evap = 0 since there is no recoverable exergy in this case.

## Slide 11
This second-law efficiency definition accounts for all irreversibilities associated within the refrigerator, including the heat transfers with the refrigerated space and the environment.
Total exergy destruction
Second-law (exergy) efficiency
T0 = TH for a refrigeration cycle

## Slide 12
SELECTING THE RIGHT REFRIGERANT
Several refrigerants may be used in refrigeration systems such as chlorofluorocarbons (CFCs), ammonia, hydrocarbons (propane, ethane, ethylene, etc.), carbon dioxide, air (in the air-conditioning of aircraft), and even water (in applications above the freezing point).
R-11, R-12, R-22, R-134a, and R-502 account for over 90 percent of the market.
The industrial and heavy-commercial sectors use ammonia (it is toxic).
R-11 is used in large-capacity water chillers serving A-C systems in buildings.
R-134a (replaced R-12, which damages ozone layer) is used in domestic refrigerators and freezers, as well as automotive air conditioners.
R-22 is used in window air conditioners, heat pumps, air conditioners of commercial buildings, and large industrial refrigeration systems, and offers strong competition to ammonia.
R-502 (a blend of R-115 and R-22) is the dominant refrigerant used in commercial refrigeration systems such as those in supermarkets.
CFCs allow more ultraviolet radiation into the earth’s atmosphere by destroying the protective ozone layer and thus contributing to the greenhouse effect that causes global warming. Fully halogenated CFCs (such as R-11, R-12, and R-115) do the most damage to the ozone layer. Refrigerants that are friendly to the ozone layer have been developed.
Two important parameters that need to be considered in the selection of a refrigerant are the temperatures of the two media (the refrigerated space and the environment) with which the refrigerant exchanges heat.

## Slide 13
HEAT PUMP SYSTEMS
The most common energy source for heat pumps is atmospheric air (air-to- air systems).
Water-source systems usually use well water and ground-source (geothermal) heat pumps use earth as the energy source. They typically have higher COPs but are more complex and more expensive to install.
Both the capacity and the efficiency of a heat pump fall significantly at low temperatures. Therefore, most air-source heat pumps require a supplementary heating system such as electric resistance heaters or a gas furnace.
Heat pumps are most competitive in areas that have a large cooling load during the cooling season and a relatively small heating load during the heating season. In these areas, the heat pump can meet the entire cooling and heating needs of residential or commercial buildings.

## Slide 15
INNOVATIVE VAPOR-COMPRESSION REFRIGERATION SYSTEMS
The simple vapor-compression refrigeration cycle is the most widely used refrigeration cycle, and it is adequate for most refrigeration applications.
The ordinary vapor-compression refrigeration systems are simple, inexpensive, reliable, and practically maintenance-free.
However, for large industrial applications efficiency, not simplicity, is the major concern.
Also, for some applications the simple vapor-compression refrigeration cycle is inadequate and needs to be modified.
For moderately and very low temperature applications some innovative refrigeration systems are used. The following cycles will be discussed:
  Cascade refrigeration systems
  Multistage compression refrigeration systems
  Multipurpose refrigeration systems with a single compressor
  Liquefaction of gases

## Slide 16
Cascade Refrigeration Systems
Some industrial applications require moderately low temperatures, and the temperature range they involve may be too large for a single vapor-compression refrigeration cycle to be practical. The solution is cascading.
Cascading improves the COP of a refrigeration system.
Some systems use three or four stages of cascading.

## Slide 17
Multistage Compression Refrigeration Systems
When the fluid used throughout the cascade refrigeration system is the same, the heat exchanger between the stages can be replaced by a mixing chamber (called a flash chamber) since it has better heat transfer characteristics.

## Slide 18
Multipurpose Refrigeration Systems with a Single Compressor
Some applications require refrigeration at more than one temperature. A practical and economical approach is to route all the exit streams from the evaporators to a single compressor and let it handle the compression process for the entire system.

## Slide 19
Liquefaction of Gases
Many important scientific and engineering processes at cryogenic temperatures (below about 100°C) depend on liquefied gases including the separation of oxygen and nitrogen from air, preparation of liquid propellants for rockets, the study of material properties at low temperatures, and the study of superconductivity.
The storage (i.e., hydrogen) and transportation of some gases (i.e., natural gas) are done after they are liquefied at very low temperatures. Several innovative cycles are used for the liquefaction of gases.

## Slide 20
GAS REFRIGERATION CYCLES
The reversed Brayton cycle (the gas refrigeration cycle) can be used for refrigeration.

## Slide 21
The gas refrigeration cycles have lower COPs relative to the vapor-compression refrigeration cycles or the reversed Carnot cycle.
The reversed Carnot cycle consumes a fraction of the net work (area 1A3B) but produces a greater amount of refrigeration (triangular area under B1).
Despite their relatively low COPs, the gas refrigeration cycles involve simple, lighter components, which make them suitable for aircraft cooling, and they can incorporate regeneration

## Slide 22
Without regeneration, the lowest turbine inlet temperature is T0, the temperature of the surroundings or any other cooling medium.
With regeneration, the high-pressure gas is further cooled to T4 before expanding in the turbine.
Lowering the turbine inlet temperature automatically lowers the turbine exit temperature, which is the minimum temperature in the cycle.
Extremely low temperatures can be achieved by repeating regeneration process.

## Slide 23
ABSORPTION REFRIGERATION SYSTEMS
Absorption refrigeration is economic when there is a source of inexpensive thermal energy at a temperature of 100 to 200°C.
Some examples include geothermal energy, solar energy, and waste heat from cogeneration or process steam plants, and even natural gas when it is at a relatively low price.

## Slide 24
Absorption refrigeration systems (ARS) involve the absorption of a refrigerant by a transport medium.
The most widely used system is the ammonia–water system, where ammonia (NH3) serves as the refrigerant and water (H2O) as the transport medium.
Other systems include water–lithium bromide and water–lithium chloride systems, where water serves as the refrigerant. These systems are limited to applications such as A-C where the minimum temperature is above the freezing point of water.
Compared with vapor-compression systems, ARS have one major advantage: A liquid is compressed instead of a vapor and as a result the work input is very small (on the order of one percent of the heat supplied to the generator) and often neglected in the cycle analysis.
ARS are often classified as heat-driven systems.
ARS are much more expensive than the vapor-compression refrigeration systems. They are more complex and occupy more space, they are much less efficient thus requiring much larger cooling towers to reject the waste heat, and they are more difficult to service since they are less common.
Therefore, ARS should be considered only when the unit cost of thermal energy is low and is projected to remain low relative to electricity.
ARS are primarily used in large commercial and industrial installations.

## Slide 25
The COP of actual absorption refrigeration systems is usually less than 1.
Air-conditioning systems based on absorption refrigeration, called absorption chillers, perform best when the heat source can supply heat at a high temperature with little temperature drop.

## Slide 26: Summary
Refrigerators and Heat Pumps
The Reversed Carnot Cycle
The Ideal Vapor-Compression Refrigeration Cycle
Actual Vapor-Compression Refrigeration Cycle
Second-law Analysis of Vapor-Compression Refrigeration Cycle
Selecting the Right Refrigerant
Heat Pump Systems
Innovative Vapor-Compression Refrigeration Systems
Gas Refrigeration Cycles
Absorption Refrigeration Systems